## Sheet1
Location | Equipment | Req. cooling (kW) | Tin (°C) | ΔT (°C) | ΔP (bar) | Flow (m3/h) | comments
south bunker | klystron | 56 | 28 | 12 | 3 | 4.0134 | worst case in summer
south bunker | accelerator | 21 | 28 | 12 | 3 | 1.505 | worst case in summer
R7 ; R8 | e+/e- selector | 4 | 24 | 20 | 6 | 0.172
R11 | Buffer Gas coils | 7.2 | 24 | 20 | 6 | 0.3096
C3; R12 | Buffer Gas Cryo Pumps | 3 | 24 | 20 | < 1 | 0.129 | 2 buffergas pumps
C4 | Trap CryoPumps | 7 | 24 | 20 | < 1 | 0.301 | 1 trap CP+1 buffergas CP
C1 | e+ trap magnet | 7 | 24 | 20 | <1 | 0.301
C2 | e+ trap duct | 7 | 24 | 20 | <1 | 0.301
C5; C6; C7;R14 | Future antiproton trap | 21 | 24 | 20 | < 1 | 0.90301 | 3 compressors
[5 empty] | total= | 7.935